# REQUEST FOR PROPOSALS

# (COMPETITIVE SEALED PROPOSALS)

SSB 1st Floor HVAC & Renovations

# RFP No:

# HHSC 26-0600

# ADDENDUM #1

for

Hawaii Health Systems Corporation 
West Hawaii Region
Kona Community Hospital

Yvonne S. Taylor, Contracts

Kona Community Hospital

79-1019 Haukapila Street

Kealakekua, HI  96750

Telephone (808) 322-9311

Fax (808) 322-4488

http://www.kch.hhsc.org/Procurement/default.aspx

An Agency of the State of Hawaii

| Revision | Date | Author | Description |
| --- | --- | --- | --- |
| Rev 000 | 30 April 2012 | N. Hida | Used 12-0226 as a template |
| Rev 001 | 16 May 2012 | N Hida | Modified after Pre-Proposal Meeting: |

ADDENDUM NO. 1

RFP No. 26-0600

SSB 1st Floor HVAC & Renovations

Kona Community Hospital

Hawaii Health Systems Corporation – West Hawaii Region

Date: April 17, 2026

This Addendum No. 1 modifies the Request for Proposals (RFP) for the above-referenced project. All other terms, conditions, requirements, and provisions of the RFP shall remain unchanged unless expressly modified herein. In the event of any conflict between this Addendum and the original RFP, this Addendum shall govern. All proposals shall be submitted in accordance with the revised requirements and schedule contained herein.

Questions and Answers

- Please confirm that all partitions, desk, and furniture will be removed prior to demolition as indicated on A001, note #3 and #5. Per the site walk, it was mentioned that there may be partitions to remain, please advise.

The only areas that the cubicles will remain is in the medical records area between the two temporary stark walls. All others will be removed by KCH

- Please confirm if attic stock of existing carpet will be available to contractors to use to patch existing flooring at new wall partitions.

Attic stock is not available.  You will need to order the carpet tile.  Any leftover tiles (full-size) shall become property of KCH.

- Please clarify the maximum allowable file size for electronic attachments. If files exceed this size limitation, please confirm that submission via a secure file-sharing link is permitted.

10MB.  As we are not permitted to utilize outside file share links, we must provide one to you.  Use this link:  https://hawaiihealthsystemcorporation.sharefile.com/r-rc5848a47cbbe4d099160e40dea359f5a .  You will need to enter your name and email address to use the link.  We recommend emailing WHRContractsMgmt@hhsc.org  after you have uploaded your proposal should there be anything wrong with the link.

- Per 3.7.3 PERSONNEL of the RFP, we are instructed to fill out Appendix K (Bid Proposal Form) for personnel, please confirm that internal resumes can be attached.

Section 3.7.3 PERSONNEL is DELETED and replaced with:

Provide explicit details on the Company’s personnel organization and staffing relative to performing requirements set forth in the Scope of Services, as follows:

A.	Company’s managerial organizational chart and resumes of key positions.

B.	Key personnel identified to perform services, including: name, years of experience, years with the Company, qualifications and verifiable references (with contact telephone numbers), if any.

- Does this work require specialized PPE or have any sterile work zone requirements and restrictions?

No, specialized PPE will not be required

- Is a infection control risk assessment required for this project? What class construction and risk categorization is this project under?

Yes, a ICRA will be performed and it will be a class III project- Major demolition in a non patient care area.

- Are the steel beams shown supporting the AHU on detail D/M301 existing with pre-drilled holes to attach the Unistrut P1001?

IE: The steel beams show are existing but there is no predrilled holes.

- Existing Office 23 has added door no.23. The ceiling in this area is listed as fire rated so does door no.23 need a fire rating as well or is rooms 22 and 23 considered 1 area?

KYA: Door No. 23 is not required to be fire rated. Rooms 22 and 23 are considered a part of the rated corridor. Walls separating them from each other or the corridor are not fire rated. Walls separating them from Rooms 24 and 19 are fire rated.

- What kind of backing and what extent is required for the new casework backing at new wall partitions at desks?

KYA: See revised backing detail 1 on Sheet A501. Assume 15 locations at 6’-0” length. The exact location and height will be determined before construction begins.

- Resilient Wall Base specification section 096513 available manufacturers states to refer to division 1 requirements. Which spec section in division 1 does this reference?

KYA: It is referencing all of Division 1 sections that apply to specification section 096513. Division 1 contains the general overall requirements for the project. The general contractor and sub-contractor shall be responsible for requirements listed in Division 1.

- General Note “B”, Drawing, M001, Notes that the contractor shall obtain and pay for applicable permits, licenses, fees and other charges for work noted. Please confirm the following;

- The Building Permit has already been applied for and processed and the Contractor is only responsible to pick it up and pay for it.

KYA:The Contractor will be responsible for picking up the Building Permit and paying for the related permit fee. Architect will be responsible for Building Permit application submittal by uploading it to EPIC on 4/16/2026.

- If the Building Permit has not been applied for, please provide approximate time frame that the permit can be picked-up.

Building permit is expected to take 3 - 4 months for review and processing before it can be picked-up.

- Equipment Schedule, Drawing, M002 specifies the Basis of Design for the Air Handler Units, Air Devices, Dampers, etc.

  - Please to support competition amongst suppliers / manufacturers on the project, please confirm that other manufacturers with representation on the Big Island and / or the State of Hawaii, can also provide air handler units, air devices, dampers, etc., that meets the intent of the project documents. Similar to other projects, equipment / material submittals will be provided for review during the submittal phase of the project.

IE: We are open to other manufactures/suppliers. The designed sequence of operation is very typical for office space, other manufacture, such as Carrier, Trane, Aaon, York can provide an equivalent product. The bidding contractor shall ensure the alternate product will meet the specification requirement,  scheduled performance and control sequence.

KYA: Fillout the Substitution Request Form provided in Section 00400 with a submittal that provides evidence the alternate product meets requirements identified in IE’s comments and requirements set in Section 01600 paragraph 2.03 for acceptable substitutions.

- We did not see any project durations or time of performance noted. If we inadvertently missed it, please furnish the location of the project duration in the documents provided.

Mandatory Questions, Page 41 asks for an approximate timeline to be submitted as a part of your proposal.  Pre-constrution activities can commence immediately after full execution of the agreement.  Construction work can commence once permit has been picked up.

- Please advise if liquidated damages are applicable and the amount per calendar day.

Yes. $250/day